## Slide 1
Vishwakarma Application ID
VK26-IITI-AHM-0210
FactoryAir Twin
pressure
+
power
→
twin
→
saving
Team Volts and Bolts
Track: ______________________
Team members: ______________________
Institution: ______________________
Faculty mentor: ______________________
Stage 2 · Design Development · October 2026 · figures from simulation unless marked real data
Working software prototype: plant overview

## Slide 2: Small factories pay for compressed air they never use
FactoryAir Twin · VK26-IITI-AHM-0210 · Problem context
compressor
Leaks hiss away day and night; no meter shows it
machines
20–30%
of compressor output is often lost to leaks
US DOE sourcebook [1]
~10%
of industrial electricity makes compressed air
US DOE sourcebook [1]
36%
of the demo plant's compressor bill buys no useful air
FactoryAir Twin, simulated
Who suffers: MSME foundries, machine shops, textile and packaging units with one or two 5–30 kW compressors, an owner, one technician and no energy manager.
Core innovation: a nightly load/unload leak test on pressure + power that teaches the twin each plant — no flow meter.
Team ID VK26-IITI-AHM-0210 · Track ______________________

## Slide 3: Today's options are too rare, too costly or brand-locked
FactoryAir Twin · VK26-IITI-AHM-0210 · Problem context
Annual leak survey
Once a year. Leaks return in weeks; the repair is never checked.
Inline flow meter
Pipe cutting and a shutdown. Says how much, not where.
Maker's monitoring
Only that brand's newer machines. Mixed rooms left out.
Electricity bill
A month late. Cannot tell production from waste.
FactoryAir Twin
Clip-on, any brand
Tests every night
Finds the zone
Prices it in ₹
Verifies the repair

## Slide 4: Before: one failed coupling costs money for weeks unseen
FactoryAir Twin · VK26-IITI-AHM-0210 · User journey
Thu 14:24
A hose coupling fails in the assembly bay
Same day
Air hisses out; the compressor loads more often
~30 days
The bill rises; the owner blames an old machine
Months
Maybe the annual survey finds it
After repair
Nobody checks the fix held
Quantified inefficiency · demo plant, 14-day twin (simulated)
₹5,580
per month added by the one failed coupling
22.5%
of compressor capacity leaking on the worst night
8.3%
of electricity spent running unloaded (₹1,094/month)
~30 days
before the bill gives the first signal

## Slide 5: After: found overnight, located at lunch, verified next night
FactoryAir Twin · VK26-IITI-AHM-0210 · User journey
23:00–05:00
Nightly leak test on pressure + power
06:00
Alert: +₹5,580/month
Lunch break
Leak Hunter: Bay 2 = 58%
Same day
Ticket, repair done
Next night
Saving measured, not promised
Chart: Nightly leak test, % of compressor capacity
| Mon 1 | Tue 2 | Wed 3 | Thu 4 | Fri 5 | Sat 6 | Sun 7 | Mon 8 | Tue 9 | Wed 10 | Thu 11 | Fri 12 | Sat 13
Leak, % of capacity | 7.3 | 7.4 | 7.5 | 22 | 22.1 | 22.1 | 22.2 | 22.3 | 22.4 | 22.5 | 8.2 | 8.2 | 8.3
new leak
repaired
1 night
to detect, vs ~30 days
~15 min
to locate the zone
₹5,453
repair saving, measured overnight
₹7,414
LPG saved by heat recovery

## Slide 6: System block diagram: two signals in, a verified saving out
FactoryAir Twin · VK26-IITI-AHM-0210 · System architecture
Sensing
4–20 mA pressure on the gauge port
Clip-on CT on one phase
Machine-on contact
Electronics
ADS1115 16-bit ADC
ESP32-S3, Wi-Fi
24 V → 5 V, microSD
Firmware (1 Hz)
mA → bar, CT → kW
Drop invalid frames
Batch → REST / MQTT, SD spool
Twin software
Validate + sensor health
Rules + ML + self-calibration
Leak Hunter, tickets, report
mA / mV
I²C
Wi-Fi
Read-only by design. No flow meter, nothing cut or shut down, and no output stage: the node physically cannot command the compressor. Everything after the ADC already runs today as the virtual edge node.

## Slide 7: Target specifications and hardware selection
FactoryAir Twin · VK26-IITI-AHM-0210 · System architecture
Parameter | Target | Selected hardware / protocol
Sampling | 1 Hz | ESP32-S3 + ADS1115 (860 SPS)
Pressure | 0–16 bar, ±0.5 % FS | 4–20 mA transmitter, 165 Ω shunt
Motor power | 0–30 A RMS | SCT-013-030 split-core CT
Data link | 10-frame batches | Wi-Fi REST; MQTT optional
Buffer | 72 h offline | microSD spool, replay
Enclosure | IP65, DIN rail | PC/ABS box, PG glands
Cost / site | < ₹10,000 | ≈ ₹6,100 indicative
Self-calibration screen: storage, leak and specific power learned from pressure + power
1.8%
mean leak error on 30 unseen plants (target ±10%)
30/30
plants within ±10% · storage error 1.9%
1 night
from a new leak to an alert (14-day twin)

## Slide 8: Mechanical design: a sealed box and a safe pressure tap
FactoryAir Twin · VK26-IITI-AHM-0210 · CAD & mechanical
Enclosure layout (concept, not CAD)
24 V PSU
5 V buck
ESP32 + ADC
microSD
PG7 glands
Pressure tap (concept)
Gauge port
→
G¼ tee
→
Ball valve
→
Transmitter
Enclosure
PC/ABS IP65
non-conductive, light, ≈ ₹700
Pressure fittings
Brass G¼, ≥ 16 bar
over 2× the 7.4 bar band
Mounting
Steel DIN rail
on the panel wall, off the vibrating frame
Stress analysis: no load-bearing part at Stage 2; pressure parts are rated fittings. Stage 3 adds a bracket vibration check.
ADD: screenshot of the team's enclosure CAD model (isometric + exploded, feature tree visible)

## Slide 9: Electronics connections and bill of materials
FactoryAir Twin · VK26-IITI-AHM-0210 · Electronics & BOM
Pressure transmitter
4–20 mA loop
CT SCT-013-030
30 A : 1 V
Machine-on contact
to GND
24 V PSU → 5 V buck
165 Ω shunt
→ ADS1115 A0
ADS1115
A1–A3 differential
ESP32-S3
SDA 8 · SCL 9 · GPIO 7
microSD · CS GPIO 10
Wi-Fi → /api/edge/ingest every 10 s; same frames the software emulator sends today
Component (qty 1 each) | ≈ ₹
ESP32-S3 DevKitC | 800
ADS1115 ADC module | 350
4–20 mA transmitter 0–16 bar | 1,800
SCT-013-030 CT | 450
Shunt, TVS, fuses | 150
24 V PSU + 5 V buck | 1,100
microSD + 16 GB card | 400
IP65 box, glands, rail | 700
G¼ tee + ball valve | 350
Total (indicative) | 6,100
Chart: Where the ₹6,100 goes
| Sensors | Controller + ADC | Power | Enclosure + fittings | Storage + protection
Cost share | 2250 | 1150 | 1100 | 1050 | 550
All parts sold by Indian online distributors; confirm prices and lead times with quotes.

## Slide 10: Maker journey: working software, built and tested by the team
FactoryAir Twin · VK26-IITI-AHM-0210 · Maker journey
Live gateway: edge node streaming firmware frames
Leak Hunter: Bay 2 carries 58% of the leakage
ADD: lab photo, team with ID badges
ADD: review photo with faculty mentor
Repository
github.com/Suheerthan/
FactoryAirTwin
124 tests
every slide number reproduced by code
Firmware
factoryair_edge.ino + wiring README
Real files
Python source, sample logger data

## Slide 11: Stage 1 → Stage 2: what we learned and changed
FactoryAir Twin · VK26-IITI-AHM-0210 · Maker journey
Real data: AI failed, physics worked
MetroPT-3 (real): the synthetic AI flagged 0 windows (AUC 0.58); the physics duty test put all 4 documented-leak nights in the top 7 of 159 (AUC 0.988)
30 minutes → 14 days
Two-week twin with shifts and nights caught the new leak the same night
"Where is it?"
Leak Hunter allocates leakage by zone, then verifies the repair
No hardware budget
Virtual edge node + firmware + CSV upload run the full pipeline today
Chart: 30 unseen plants: estimated vs hidden true leak (m³/min)
| 0.2714 | 0.1475 | 0.2019 | 0.28 | 0.305 | 0.0506 | 0.0689 | 0.148 | 0.1489 | 0.1879 | 0.2448 | 0.231 | 0.2786 | 0.3047 | 0.2542 | 0.2633 | 0.1582 | 0.1605 | 0.2632 | 0.2308 | 0.2663 | 0.1333 | 0.0331 | 0.2009 | 0.2985 | 0.246 | 0.1623 | 0.0529 | 0.1152 | 0.135
Estimated leak | 0.2755 | 0.1445 | 0.2034 | 0.2951 | 0.3181 | 0.0491 | 0.0697 | 0.1474 | 0.1504 | 0.1904 | 0.2419 | 0.2341 | 0.2835 | 0.3035 | 0.2543 | 0.2698 | 0.1583 | 0.1676 | 0.266 | 0.2279 | 0.2593 | 0.1336 | 0.0339 | 0.2031 | 0.2997 | 0.2541 | 0.1586 | 0.0519 | 0.1139 | 0.1417
Mean error 1.8% · storage 1.9% · all 30 within ±10% (simulated)
ADD: faculty sign-off (name, department, college)

## Slide 12: Safety by design: read-only, clip-on, fail-quiet
FactoryAir Twin · VK26-IITI-AHM-0210 · Safety & hazard mitigation
No output stage
cannot start, stop or reload the compressor
Clip-on CT
no mains conductor opened
Isolated tap
ball valve, fittings rated > 2× pressure
Sealed + fused
IP65 box, fused 24 V supply
Failure mode | Hazard | Built-in protection
Transmitter open loop / drift | Wrong leak figure | < 3.6 mA frames dropped; stuck and range checks first
Wi-Fi dropout | Lost data | 72 h SD spool; gaps flagged
Clock jump / bad frame | Corrupt history | Ingest rejects them (tested live)
False leak alarm | Wasted labour | Two estimators must agree; weak nights graded down
Wrong nameplate FAD | Biased ₹ | Shown openly; Stage 3 pump-up test
Standards considered
IEC 61010-1, 61010-2-032
IEC 60529 (IP65)
ISO 11011 (air audits)
IS 2379 (pipe colours)

## Slide 13: Four-month plan to a field-tested prototype
FactoryAir Twin · VK26-IITI-AHM-0210 · Roadmap
Nov 2026
Build: assemble node, flash firmware, bench-test vs gauge + clamp meter
Dec 2026
Integrate: enclosure CAD + fit-out, college compressor install
Jan 2027
Validate: MSME pilot vs manual leak-down + ultrasonic walk
Feb 2027
Prove: site recalibration, repair a found leak, verify overnight
Stage 3 commitment: demonstrated live on this dashboard
A working edge node on a real compressor
A nightly leak index from real data
One leak located, repaired and verified overnight

## Slide 14: Engineering bottlenecks we hit in simulation
FactoryAir Twin · VK26-IITI-AHM-0210 · Technical challenges & risks
A leak looks like demand
Daytime data cannot separate production air from leaks.
Nameplate is not the truth
3% low delivery biased estimates by ~3%.
Synthetic AI does not transfer
MetroPT-3: 0 windows flagged, AUC 0.58. The physics test scored 0.988.
No quiet hours
24×7 plants give the nightly test no window.
Valves are not perfect
Seeping valve seats blur the zone split.
Field data is messy
Dropouts, stuck sensors, spikes, clock jumps.

## Slide 15: Backup solutions for each risk
FactoryAir Twin · VK26-IITI-AHM-0210 · Technical challenges & risks
Risk
Primary solution
Fallback
Leak vs demand
Test only in idle windows via the machine-on contact
Weekend leak-down test
Nameplate bias
One-time pump-up test measures real FAD
Show the bias band on every ₹
AI transfer gap
Physics sets all ₹: AUC 0.988 on real MetroPT-3 nights
Per-site model recalibration
No quiet hours
Lunch-break tests; decay-only mode
Isolation during planned stops
Seeping valves
Survey both directions and compare
Ultrasonic walk in the top zone
Already verified in simulation: the repeat valve survey measured ₹4,276/month vs ₹4,741 predicted (−9.8%, 92% repair efficacy).

## Slide 16: References and sources
FactoryAir Twin · VK26-IITI-AHM-0210 · References
[1] U.S. Department of Energy & Compressed Air Challenge, Improving Compressed Air System Performance: A Sourcebook for Industry (3rd ed.).
[2] ISO 11011:2013, Compressed air — Energy efficiency — Assessment.
[3] Bureau of Energy Efficiency (India), Energy Efficiency in Electrical Utilities, Chapter 3: Compressed Air System.
[4] Veloso, B. et al., "The MetroPT dataset for predictive maintenance", Scientific Data 9, 764 (2022); UCI Machine Learning Repository, MetroPT-3 (id 791).
[5] IEC 61010-1, IEC 61010-2-032 (measurement equipment, current clamps); IEC 60529 (IP code).
[6] IS 2379, Pipelines — Identification colour code (Bureau of Indian Standards).
[7] Data sheets: Espressif ESP32-S3, Texas Instruments ADS1115, YHDC SCT-013 series.
Images: screenshots of the team's own software; diagrams drawn by the team; icons from the open-source Tabler Icons set (MIT licence).