## Slide 1
Vishwakarma Application ID
VK26-IITI-AHM-0210
FactoryAir Twin
A self-calibrating digital twin that finds, locates, prices and verifies compressed-air waste using only the two signals a small factory already has: header pressure and motor power.
Team Volts and Bolts
Track: ______________________
Team members: ______________________
Institution: ______________________
Faculty mentor: ______________________
Stage 2 · Design Development · October 2026 · all figures from simulation unless marked real data
Working software prototype: plant overview screen

## Slide 2: Small factories pay for compressed air they never use
FactoryAir Twin · VK26-IITI-AHM-0210 · Problem context
Project overview
Title: FactoryAir Twin
Team ID: VK26-IITI-AHM-0210
Track: ______________________
Core innovation
A nightly load/unload leak test on header pressure and motor power that teaches the twin each plant's own storage volume, leak flow and specific power — so it can find, locate and verify leaks with no flow meter.
Reads only. It never sends a command to the compressor.
Problem statement
Leaks, unloaded running and excess pressure waste a large share of compressor electricity. Nobody sees it: there is no flow meter on the line, the bill arrives a month later, and an air leak makes no smoke or smell.
Target beneficiary
MSME units — foundries, machine shops, textile and packaging plants — running one or two 5–30 kW screw compressors, with an owner and one maintenance person and no energy manager.
20–30%
of compressor output is often lost to leaks
US DOE sourcebook [1]
~10%
of industrial electricity makes compressed air
US DOE sourcebook [1]
36%
of the demo plant's compressor bill buys no useful air
FactoryAir Twin, simulated

## Slide 3: Today's options are too rare, too costly or brand-locked
FactoryAir Twin · VK26-IITI-AHM-0210 · Problem context
Option a small plant has today | What it needs | What it misses
Annual ultrasonic leak survey | A consultant visit | A snapshot once a year. New leaks run unseen for months; no one checks the repair held.
Inline flow meter | Pipe cutting and a shutdown | Says how much air flows, not where it leaks or what it costs.
Compressor maker's connected monitoring | That brand's newer machine | Older and mixed-brand compressor rooms — most small plants — are left out.
Watching the electricity bill | Nothing | Arrives a month late and cannot separate production from waste.
FactoryAir Twin | Two clip-on signals, any brand | Tests every night, finds the zone, prices it in ₹, and measures the repair the next night.
The gap: nobody measures waste continuously, cheaply and on any compressor — so it stays invisible until the bill.

## Slide 4: Before: one failed coupling costs money for weeks unseen
FactoryAir Twin · VK26-IITI-AHM-0210 · User journey
Thu, 14:24
A hose coupling fails in the assembly bay
Same day
The compressor quietly loads more often. No alarm, no flow meter
~30 days
The electricity bill rises. The owner blames an old machine
Months
Maybe the annual survey finds it, maybe not
After repair
Nobody measures whether the fix held
Quantified inefficiency in the demo plant (14-day twin, simulated)
₹5,580
a month added by the one failed coupling
22.5%
of compressor capacity leaking at the worst night
8.3%
of electricity spent running unloaded (₹1,094/month)
~30 days
until the bill is the first signal: the leak costs a full month before anyone looks

## Slide 5: After: found overnight, located at lunch, verified next night
FactoryAir Twin · VK26-IITI-AHM-0210 · User journey
23:00–05:00
Nightly leak test on pressure + power
06:00
Alert to the maintenance group: +₹5,580/month
Lunch break
Leak Hunter: 5 valve tests, ~15 min → Bay 2 = 58%
Same day
Ticket raised, repair done
Next night
Saving measured, not promised
Chart: Nightly leak test, % of compressor capacity
| Mon 1 | Tue 2 | Wed 3 | Thu 4 | Fri 5 | Sat 6 | Sun 7 | Mon 8 | Tue 9 | Wed 10 | Thu 11 | Fri 12 | Sat 13
Leak, % of capacity (nightly test) | 7.3 | 7.4 | 7.5 | 22 | 22.1 | 22.1 | 22.2 | 22.3 | 22.4 | 22.5 | 8.2 | 8.2 | 8.3
new leak (Thu 4)
repaired (Thu 11)
Quantified efficiency (simulated)
Detection
next morning
vs ~30 days
Locating the zone
~15 min
5 decay tests
Repair saving
₹5,453/mo
measured overnight
Zone ticket
₹4,276/mo
measured vs ₹4,741 predicted
Heat recovery
₹7,414/mo
LPG displaced, 8.8-month payback
New flow meters
0
pressure + power only

## Slide 6: System block diagram: two signals in, a verified saving out
FactoryAir Twin · VK26-IITI-AHM-0210 · System architecture
Mechanical & sensing
4–20 mA pressure transmitter, 0–16 bar, on the existing gauge port behind a ball valve
Split-core CT on one motor phase: clip-on, no cable opened
Optional machine-on dry contact
Electronics & power
ADS1115 16-bit ADC, 165 Ω 0.1 % shunt
ESP32-S3 controller, Wi-Fi
24 V DIN supply → 5 V buck
microSD buffer · no output stage
Firmware logic (1 Hz)
Read loop current → bar; CT RMS → kW
Drop invalid frames (open loop, no clock)
Batch 10 frames → REST / MQTT
Spool to SD offline, replay oldest-first
Twin software (laptop, offline)
Ingest & validate → sensor health
Rules + Isolation Forest + Random Forest
Nightly self-calibration (leak, volume, kW per m³/min)
Leak Hunter · advisors · tickets · owner report
Architecture rationale: a clip-on CT and a gauge-port transmitter instead of a flow meter, so nothing is cut or shut down. Everything after the ADC is software, so today's virtual edge node already exercises the full pipeline the hardware will feed. The node has no output stage at all: it physically cannot command the compressor.

## Slide 7: Target specifications and hardware selection
FactoryAir Twin · VK26-IITI-AHM-0210 · System architecture
Parameter | Target specification | Selected hardware / protocol
Sampling | 1 Hz pressure and power | ESP32-S3 + ADS1115 at 860 samples/s
Header pressure | 0–16 bar(g), ±0.5 % full scale | 4–20 mA transmitter, 165 Ω 0.1 % shunt
Motor power | 0–30 A per phase, RMS | SCT-013-030 split-core CT, RMS over 10 mains cycles
Data link | Batches of 10 frames, read-only | Wi-Fi REST to /api/edge/ingest; MQTT optional
Offline buffer | 72 h at 1 Hz | microSD spool, replayed oldest-first
Enclosure & supply | IP65, DIN rail | PC/ABS box, PG glands, 24 V DIN PSU → 5 V
Cost per site | under ₹10,000 | ≈ ₹6,100 indicative bill of materials
Software targets, tested
1.8%
mean leak error on 30 random plants the twin had never seen (target ±10%)
30/30
plants within ±10% · storage error 1.9%, specific power 2.2%
1 night
from a new leak to an alert, in the 14-day plant twin
All software results are from simulation; field accuracy is a Stage 3 deliverable.

## Slide 8: Mechanical design: a sealed box and a safe pressure tap
FactoryAir Twin · VK26-IITI-AHM-0210 · CAD & mechanical
Enclosure layout (concept, not CAD)
24 V PSU
5 V buck
ESP32-S3 + ADS1115 carrier
microSD
PG7 glands: CT, transmitter, contact
Pressure tap (concept)
Gauge port
G¼ tee
Ball valve
Transmitter
Part | Options weighed | Choice and reason
Enclosure | Aluminium · ABS · PC/ABS | PC/ABS IP65: non-conductive near mains, light, ≈ ₹700
Pressure fittings | Push-fit nylon · brass · SS304 | Brass G¼ rated ≥ 16 bar: over 2× the 7.4 bar band, relief-protected
Mounting | Magnet · screws · DIN rail | Steel DIN rail on the panel wall: away from compressor vibration
Stress analysis: no load-bearing structure at Stage 2. The only pressure-retaining parts are off-the-shelf fittings rated above twice the working pressure. Stage 3 adds a vibration check of the bracket next to the compressor.
ADD: screenshot of the team's enclosure CAD model (isometric + exploded view, feature tree visible)

## Slide 9: Electronics connections and bill of materials
FactoryAir Twin · VK26-IITI-AHM-0210 · Electronics & BOM
Connection diagram (wiring plan)
Pressure transmitter
4–20 mA, 24 V loop
165 Ω shunt
0.66–3.30 V
CT SCT-013-030
30 A : 1 V
Machine-on contact
dry, to GND
ADS1115
A0 · A1–A3 diff.
ESP32-S3
GPIO8 SDA · GPIO9 SCL
GPIO7 contact · GPIO10 SD CS
24 V PSU → 5 V buck
microSD (SPI)
Component | Qty | ≈ ₹
ESP32-S3 DevKitC | 1 | 800
ADS1115 16-bit ADC module | 1 | 350
4–20 mA transmitter 0–16 bar | 1 | 1,800
SCT-013-030 split-core CT | 1 | 450
165 Ω 0.1 % shunt, TVS, fuses | 1 | 150
24 V DIN PSU + 5 V buck | 1 | 1,100
microSD module + 16 GB card | 1 | 400
IP65 box, glands, DIN rail | 1 | 700
G¼ brass tee + ball valve | 1 | 350
Total (indicative) |  | 6,100
Sourcing: every part is sold by Indian online electronics and pneumatics distributors; prices and lead times to be confirmed with vendor quotes before ordering.

## Slide 10: Maker journey: working software, built and tested by the team
FactoryAir Twin · VK26-IITI-AHM-0210 · Maker journey
Live gateway: virtual edge node streaming real firmware frames, one impossible spike rejected
Leak Hunter: guided valve survey finds Bay 2 carries 58% of the leakage
ADD: lab photo of team members with ID badges
ADD: joint review photo with faculty mentor
Repository: github.com/Suheerthan/FactoryAirTwin
Native files: Python source, firmware/factoryair_edge/factoryair_edge.ino, firmware/README.md (wiring, BOM), test suite
Evidence: 124 automated tests pass · every number on these slides is reproduced by the code · commit timestamps show Stage 2 work

## Slide 11: Stage 1 → Stage 2: what we learned and changed
FactoryAir Twin · VK26-IITI-AHM-0210 · Maker journey
1
Real data humbled the AI
On 1.5 million real MetroPT-3 readings the synthetic anomaly threshold flagged 0 windows (AUC 0.58). So money figures now come from a physics test that learns each plant.
2
30 minutes → 14 days
A two-week plant twin with shifts, nights and Sundays runs the leak test every night and caught the new leak the same night.
3
"Where is it?"
Leak Hunter uses the plant's own branch valves to allocate leakage by zone, then verifies the repair with a repeat survey.
4
No hardware budget
Virtual edge node, ESP32 firmware and CSV upload: the full pipeline runs today without the box.
Chart: 30 unseen plants: estimated vs hidden true leak (m³/min)
| 0.2714 | 0.1475 | 0.2019 | 0.28 | 0.305 | 0.0506 | 0.0689 | 0.148 | 0.1489 | 0.1879 | 0.2448 | 0.231 | 0.2786 | 0.3047 | 0.2542 | 0.2633 | 0.1582 | 0.1605 | 0.2632 | 0.2308 | 0.2663 | 0.1333 | 0.0331 | 0.2009 | 0.2985 | 0.246 | 0.1623 | 0.0529 | 0.1152 | 0.135
Estimated leak | 0.2755 | 0.1445 | 0.2034 | 0.2951 | 0.3181 | 0.0491 | 0.0697 | 0.1474 | 0.1504 | 0.1904 | 0.2419 | 0.2341 | 0.2835 | 0.3035 | 0.2543 | 0.2698 | 0.1583 | 0.1676 | 0.266 | 0.2279 | 0.2593 | 0.1336 | 0.0339 | 0.2031 | 0.2997 | 0.2541 | 0.1586 | 0.0519 | 0.1139 | 0.1417
Mean error 1.8% · storage volume 1.9% · all 30 within ±10% (simulated)
ADD: faculty sign-off line (name, department, college)

## Slide 12: Safety by design: read-only, clip-on, fail-quiet
FactoryAir Twin · VK26-IITI-AHM-0210 · Safety & hazard mitigation
No output stage
The node has no relay or analogue output: it cannot start, stop or reload the compressor.
Clip-on current sensing
No mains conductor is opened; the CT's built-in burden avoids open-secondary voltage.
Isolated pressure tap
Transmitter sits behind a ball valve on a fitting rated above 2× working pressure.
Fused, sealed supply
Fused 24 V DIN supply inside an IP65 box with glands.
Failure mode | Hazard | Built-in protection
Transmitter open loop / drift | Wrong leak figure | < 3.6 mA frames dropped; stuck-signal and range checks before any scoring
Wi-Fi dropout | Lost data | 72 h SD spool; gaps flagged by sensor health
Clock jumps / bad frame | Corrupt history | Ingest rejects non-increasing time and impossible values (tested)
False leak alarm | Wasted labour | Two independent estimators must agree; low-confidence nights are graded down
Wrong nameplate FAD | Biased ₹ | Shown openly; Stage 3 pump-up test calibrates FAD once
Unauthorised change | Bad settings | Role-gated API: operators cannot change calibration
Standards considered: IEC 61010-1 and IEC 61010-2-032 (measurement equipment, current clamps) · IEC 60529 (IP65) · ISO 11011 (compressed-air energy assessment) · IS 2379 (pipe colour coding, used in the UI)

## Slide 13: Four-month plan to a field-tested prototype
FactoryAir Twin · VK26-IITI-AHM-0210 · Roadmap
Month 1 · Nov 2026
Build
Order parts, assemble node on a breadboard
Flash firmware; bench-test against a calibrated gauge and clamp meter
Month 2 · Dec 2026
Integrate
Enclosure CAD and print/fit-out
Install on a college workshop compressor; stream to the twin
Month 3 · Jan 2027
Validate
Pilot at one MSME unit
Compare nightly test with a manual leak-down test and an ultrasonic walk
Month 4 · Feb 2027
Prove
Recalibrate on site data; one-time FAD pump-up test
Repair a found leak and verify the saving overnight
Stage 3 commitment: a working edge node on a real compressor, a nightly leak index from real data, one located and repaired leak with its saving measured — demonstrated live on the same dashboard shown here.

## Slide 14: Engineering bottlenecks we hit in simulation
FactoryAir Twin · VK26-IITI-AHM-0210 · Technical challenges & risks
A leak looks like demand
With no flow meter, extra production air and a leak raise the same signal. Daytime data alone cannot separate them.
Nameplate is not the truth
A machine delivering 3% below nameplate biased leak and storage estimates by about 3% in the 14-day twin.
Synthetic AI does not transfer
MetroPT-3: 0 real windows flagged by the synthetic threshold, AUC 0.58. Good on simulation is not good in the field.
No quiet hours
Plants running 24×7 never idle, so the nightly test has no window.
Valves are not perfect
Leak Hunter assumes tight valve seats; seeping valves blur the zone split.
Field data is messy
Wi-Fi drops, stuck transmitters, impossible spikes and clock jumps. The Live gateway injects all four; each one must be caught before any scoring.

## Slide 15: Backup solutions for each risk
FactoryAir Twin · VK26-IITI-AHM-0210 · Technical challenges & risks
Risk | Primary solution | Fallback
Leak vs demand | Test only in idle windows (night, lunch) using the machine-on contact | Weekend leak-down test scheduled from the dashboard
Nameplate bias | One-time pump-up test at install to measure real FAD | Show the bias band openly on every ₹ figure
AI transfer gap | Physics self-calibration sets all ₹ figures; ML only ranks anomalies | Per-site recalibration of the anomaly model (recalibrate.py)
No quiet hours | Short lunch-break tests + decay-only mode with known volume | Branch-valve isolation during planned stops
Seeping valves | Two-direction survey (open-up and close-down) and compare | Repeat the decay test; ultrasonic walk in the top zone
Already verified in simulation: Leak Hunter's repeat-survey check measured ₹4,276/month against ₹4,741 predicted (−9.8%, explained by 92% repair efficacy).

## Slide 16: References and sources
FactoryAir Twin · VK26-IITI-AHM-0210 · References
[1] U.S. Department of Energy & Compressed Air Challenge, Improving Compressed Air System Performance: A Sourcebook for Industry (3rd ed.).
[2] ISO 11011:2013, Compressed air — Energy efficiency — Assessment.
[3] Bureau of Energy Efficiency (India), Energy Efficiency in Electrical Utilities, Chapter 3: Compressed Air System.
[4] Veloso, B. et al., "The MetroPT dataset for predictive maintenance", Scientific Data 9, 764 (2022); UCI Machine Learning Repository, MetroPT-3 Dataset (id 791).
[5] IEC 61010-1 and IEC 61010-2-032 (safety of measurement equipment and hand-held current clamps); IEC 60529 (degrees of protection, IP code).
[6] IS 2379, Pipelines — Identification colour code (Bureau of Indian Standards).
[7] Component data sheets: Espressif ESP32-S3, Texas Instruments ADS1115, YHDC SCT-013 series.
Images: all screenshots are of the team's own FactoryAir Twin software; diagrams drawn by the team. No third-party images used.